## SC Horizontal W meter
Hudevad SC Horizontal
Type |  |  | SCE (single) |  | SCD (double) |  | SCE (single) |  | SCD (double) |  | SCE (single) |  | SCD (double) |  | SCE (single) |  | SCD (double) |  | SCE (single) |  | SCD (double) |  | SCE (single) |  | SCD (double) |  | SCE (single) |  | SCD (double)
Height |  |  | 400 |  |  |  | 500 |  |  |  | 600 |  |  |  | 700 |  |  |  | 800 |  |  |  | 900 |  |  |  | 1000
Element distance |  |  | 40 | 60 | 40 | 60 | 40 | 60 | 40 | 60 | 40 | 60 | 40 | 60 | 40 | 60 | 40 | 60 | 40 | 60 | 40 | 60 | 40 | 60 | 40 | 60 | 40 | 60 | 40 | 60
W/m at 75/65/20 |  |  | 753 | 590 | 1225 | 942 | 908 | 707 | 1483 | 1151 | 1058 | 821 | 1738 | 1355 | 1208 | 933 | 1990 | 1557 | 1355 | 1046 | 2240 | 1751 | 1505 | 1158 | 2488 | 1955 | 1653 | 1270 | 2725 | 2159
n-coefficients |  |  | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3
Weight/Element |  |  | 1.1 |  | 2 |  | 1.4 |  | 2.4 |  | 1.6 |  | 2.9 |  | 1.8 |  | 3.4 |  | 2.1 |  | 3.8 |  | 2.3 |  | 4.3 |  | 2.5 |  | 4.7
Water Content/Element |  |  | 0.3 |  | 0.4 |  | 0.3 |  | 0.5 |  | 0.4 |  | 0.6 |  | 0.4 |  | 0.7 |  | 0.5 |  | 0.8 |  | 0.5 |  | 0.9 |  | 0.6 |  | 1
Table of heat outputs at:
Arithmetic |  |  | Logarithmic |  |  | Watt to Btu/h:
Inlet | 75 | ° C | 75 |  | 75 | 3.412
Outlet | 65 | ° C | 65 |  | 65
Ambient | 20 | ° C | 20 |  | 20
Delta T | 50 | ° C | 49.8329 |  | 49.8329
Advisory recommendation for the choice of calculation method and use of reduction factor:
Logarithmic conversion should be used on emitters up until and including height 400mm, as well as on low convectors.
The logarithmic calculation method should also be used if the relative cooling surpasses 75%.
Arithmetic conversion should be used on emitters above height 400mm if the relative cooling is under 75%.
Arithmetic outputs
W/meter | SCE single |  | SCD Double
Height | Element spacing
| 40 | 60 | 40 | 60
400 | 753 | 590 | 1225 | 942
500 | 908 | 707 | 1483 | 1151
600 | 1058 | 821 | 1738 | 1355
700 | 1208 | 933 | 1990 | 1557
800 | 1355 | 1046 | 2240 | 1751
900 | 1505 | 1158 | 2488 | 1955
1000 | 1653 | 1270 | 2725 | 2159
Conversion to Logarithmic Outputs
W/meter | SCE single |  | SCD Double
Height | Element spacing
| 40 | 60 | 40 | 60
400 | 753 | 590 | 1225 | 942
500 | 908 | 707 | 1483 | 1151
600 | 1058 | 821 | 1738 | 1355
700 | 1208 | 933 | 1990 | 1557
800 | 1355 | 1046 | 2240 | 1751
900 | 1505 | 1158 | 2488 | 1955
1000 | 1653 | 1270 | 2725 | 2159
Conversion to Btu/hr
W/meter | SCE single |  | SCD Double
Height | Element spacing
| 40 | 60 | 40 | 60
400 | 2569.236 | 2013.08 | 4179.7 | 3214.104
500 | 3098.096 | 2412.284 | 5059.996 | 3927.212
600 | 3609.896 | 2801.252 | 5930.056 | 4623.26
700 | 4121.696 | 3183.396 | 6789.88 | 5312.484
800 | 4623.26 | 3568.952 | 7642.88 | 5974.412
900 | 5135.06 | 3951.096 | 8489.056 | 6670.46
1000 | 5640.036 | 4333.24 | 9297.7 | 7366.508

## SC Horizontal All sizes
Hudevad SC Horizontal
Type |  |  | SCE (single) |  | SCD (double) |  | SCE (single) |  | SCD (double) |  | SCE (single) |  | SCD (double) |  | SCE (single) |  | SCD (double) |  | SCE (single) |  | SCD (double) |  | SCE (single) |  | SCD (double) |  | SCE (single) |  | SCD (double)
Height |  |  | 400 |  |  |  | 500 |  |  |  | 600 |  |  |  | 700 |  |  |  | 800 |  |  |  | 900 |  |  |  | 1000
Element distance |  |  | 40 | 60 | 40 | 60 | 40 | 60 | 40 | 60 | 40 | 60 | 40 | 60 | 40 | 60 | 40 | 60 | 40 | 60 | 40 | 60 | 40 | 60 | 40 | 60 | 40 | 60 | 40 | 60
W/m at 75/65/20 |  |  | 753 | 590 | 1225 | 942 | 908 | 707 | 1483 | 1151 | 1058 | 821 | 1738 | 1355 | 1208 | 933 | 1990 | 1557 | 1355 | 1046 | 2240 | 1751 | 1505 | 1158 | 2488 | 1955 | 1653 | 1270 | 2725 | 2159
n-coefficients |  |  | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3
Weight/Element |  |  | 1.1 |  | 2 |  | 1.4 |  | 2.4 |  | 1.6 |  | 2.9 |  | 1.8 |  | 3.4 |  | 2.1 |  | 3.8 |  | 2.3 |  | 4.3 |  | 2.5 |  | 4.7
Water Content/Element |  |  | 0.3 |  | 0.4 |  | 0.3 |  | 0.5 |  | 0.4 |  | 0.6 |  | 0.4 |  | 0.7 |  | 0.5 |  | 0.8 |  | 0.5 |  | 0.9 |  | 0.6 |  | 1
Table of heat outputs at:
Arithmetic |  |  | Logarithmic |  |  | Watt to Btu/h:
Inlet | 75 | ° C | 75 |  | 75 | 3.412
Outlet | 65 | ° C | 65 |  | 65
Ambient | 20 | ° C | 20 |  | 20
Delta T | 50 | ° C | 49.8329 |  | 49.8329
Advisory recommendation for the choice of calculation method and use of reduction factor:
Logarithmic conversion should be used on emitters up until and including height 400mm, as well as on low convectors.
The logarithmic calculation method should also be used if the relative cooling surpasses 75%.
Arithmetic conversion should be used on emitters above height 400mm if the relative cooling is under 75%.
Arithmetic outputs
Type |  |  | SCE (single) |  | SCD (double) |  | SCE (single) |  | SCD (double) |  | SCE (single) |  | SCD (double) |  | SCE (single) |  | SCD (double) |  | SCE (single) |  | SCD (double) |  | SCE (single) |  | SCD (double) |  | SCE (single) |  | SCD (double)
Height |  |  | 400 |  |  |  | 500 |  |  |  | 600 |  |  |  | 700 |  |  |  | 800 |  |  |  | 900 |  |  |  | 1000
Element spacing |  |  | 40 | 60 | 40 | 60 | 40 | 60 | 40 | 60 | 40 | 60 | 40 | 60 | 40 | 60 | 40 | 60 | 40 | 60 | 40 | 60 | 40 | 60 | 40 | 60 | 40 | 60 | 40 | 60
Length
400 |  |  | 301 | 236 | 490 | 377 | 363 | 283 | 593 | 460 | 423 | 328 | 695 | 542 | 483 | 373 | 796 | 623 | 542 | 418 | 896 | 700 | 602 | 463 | 995 | 782 | 661 | 508 | 1090 | 864
440 |  |  | 331 |  | 539 |  | 400 |  | 653 |  | 466 |  | 765 |  | 532 |  | 876 |  | 596 |  | 986 |  | 662 |  | 1095 |  | 727 |  | 1199
460 |  |  |  | 271 |  | 433 |  | 325 |  | 529 |  | 378 |  | 623 |  | 429 |  | 716 |  | 481 |  | 805 |  | 533 |  | 899 |  | 584 |  | 993
480 |  |  | 361 |  | 588 |  | 436 |  | 712 |  | 508 |  | 834 |  | 580 |  | 955 |  | 650 |  | 1075 |  | 722 |  | 1194 |  | 793 |  | 1308
520 |  |  | 392 | 307 | 637 | 490 | 472 | 368 | 771 | 599 | 550 | 427 | 904 | 705 | 628 | 485 | 1035 | 810 | 705 | 544 | 1165 | 911 | 783 | 602 | 1294 | 1017 | 860 | 660 | 1417 | 1123
560 |  |  | 422 |  | 686 |  | 508 |  | 830 |  | 592 |  | 973 |  | 676 |  | 1114 |  | 759 |  | 1254 |  | 843 |  | 1393 |  | 926 |  | 1526
580 |  |  |  | 342 |  | 546 |  | 410 |  | 668 |  | 476 |  | 786 |  | 541 |  | 903 |  | 607 |  | 1016 |  | 672 |  | 1134 |  | 737 |  | 1252
600 |  |  | 452 |  | 735 |  | 545 |  | 890 |  | 635 |  | 1043 |  | 725 |  | 1194 |  | 813 |  | 1344 |  | 903 |  | 1493 |  | 992 |  | 1635
640 |  |  | 482 | 378 | 784 | 603 | 581 | 452 | 949 | 737 | 677 | 525 | 1112 | 867 | 773 | 597 | 1274 | 996 | 867 | 669 | 1434 | 1121 | 963 | 741 | 1592 | 1251 | 1058 | 813 | 1744 | 1382
680 |  |  | 512 |  | 833 |  | 617 |  | 1008 |  | 719 |  | 1182 |  | 821 |  | 1353 |  | 921 |  | 1523 |  | 1023 |  | 1692 |  | 1124 |  | 1853
700 |  |  |  | 413 |  | 659 |  | 495 |  | 806 |  | 575 |  | 949 |  | 653 |  | 1090 |  | 732 |  | 1226 |  | 811 |  | 1369 |  | 889 |  | 1511
720 |  |  | 542 |  | 882 |  | 654 |  | 1068 |  | 762 |  | 1251 |  | 870 |  | 1433 |  | 976 |  | 1613 |  | 1084 |  | 1791 |  | 1190 |  | 1962
760 |  |  | 572 | 448 | 931 | 716 | 690 | 537 | 1127 | 875 | 804 | 624 | 1321 | 1030 | 918 | 709 | 1512 | 1183 | 1030 | 795 | 1702 | 1331 | 1144 | 880 | 1891 | 1486 | 1256 | 965 | 2071 | 1641
800 |  |  | 602 |  | 980 |  | 726 |  | 1186 |  | 846 |  | 1390 |  | 966 |  | 1592 |  | 1084 |  | 1792 |  | 1204 |  | 1990 |  | 1322 |  | 2180
820 |  |  |  | 484 |  | 772 |  | 580 |  | 944 |  | 673 |  | 1111 |  | 765 |  | 1277 |  | 858 |  | 1436 |  | 950 |  | 1603 |  | 1041 |  | 1770
840 |  |  | 633 |  | 1029 |  | 763 |  | 1246 |  | 889 |  | 1460 |  | 1015 |  | 1672 |  | 1138 |  | 1882 |  | 1264 |  | 2090 |  | 1389 |  | 2289
880 |  |  | 663 | 519 | 1078 | 829 | 799 | 622 | 1305 | 1013 | 931 | 722 | 1529 | 1192 | 1063 | 821 | 1751 | 1370 | 1192 | 920 | 1971 | 1541 | 1324 | 1019 | 2189 | 1720 | 1455 | 1118 | 2398 | 1900
920 |  |  | 693 |  | 1127 |  | 835 |  | 1364 |  | 973 |  | 1599 |  | 1111 |  | 1831 |  | 1247 |  | 2061 |  | 1385 |  | 2289 |  | 1521 |  | 2507
940 |  |  |  | 555 |  | 885 |  | 665 |  | 1082 |  | 772 |  | 1274 |  | 877 |  | 1464 |  | 983 |  | 1646 |  | 1089 |  | 1838 |  | 1194 |  | 2029
960 |  |  | 723 |  | 1176 |  | 872 |  | 1424 |  | 1016 |  | 1668 |  | 1160 |  | 1910 |  | 1301 |  | 2150 |  | 1445 |  | 2388 |  | 1587 |  | 2616
1000 |  |  | 753 | 590 | 1225 | 942 | 908 | 707 | 1483 | 1151 | 1058 | 821 | 1738 | 1355 | 1208 | 933 | 1990 | 1557 | 1355 | 1046 | 2240 | 1751 | 1505 | 1158 | 2488 | 1955 | 1653 | 1270 | 2725 | 2159
1040 |  |  | 783 |  | 1274 |  | 944 |  | 1542 |  | 1100 |  | 1808 |  | 1256 |  | 2070 |  | 1409 |  | 2330 |  | 1565 |  | 2588 |  | 1719 |  | 2834
1060 |  |  |  | 625 |  | 999 |  | 749 |  | 1220 |  | 870 |  | 1436 |  | 989 |  | 1650 |  | 1109 |  | 1856 |  | 1227 |  | 2072 |  | 1346 |  | 2289
1080 |  |  | 813 |  | 1323 |  | 981 |  | 1602 |  | 1143 |  | 1877 |  | 1305 |  | 2149 |  | 1463 |  | 2419 |  | 1625 |  | 2687 |  | 1785 |  | 2943
1120 |  |  | 843 | 661 | 1372 | 1055 | 1017 | 792 | 1661 | 1289 | 1185 | 920 | 1947 | 1518 | 1353 | 1045 | 2229 | 1744 | 1518 | 1172 | 2509 | 1961 | 1686 | 1297 | 2787 | 2190 | 1851 | 1422 | 3052 | 2418
1160 |  |  | 873 |  | 1421 |  | 1053 |  | 1720 |  | 1227 |  | 2016 |  | 1401 |  | 2308 |  | 1572 |  | 2598 |  | 1746 |  | 2886 |  | 1917 |  | 3161
1180 |  |  |  | 696 |  | 1112 |  | 834 |  | 1358 |  | 969 |  | 1599 |  | 1101 |  | 1837 |  | 1234 |  | 2066 |  | 1366 |  | 2307 |  | 1499 |  | 2548
1200 |  |  | 904 |  | 1470 |  | 1090 |  | 1780 |  | 1270 |  | 2086 |  | 1450 |  | 2388 |  | 1626 |  | 2688 |  | 1806 |  | 2986 |  | 1984 |  | 3270
1240 |  |  | 934 | 732 | 1519 | 1168 | 1126 | 877 | 1839 | 1427 | 1312 | 1018 | 2155 | 1680 | 1498 | 1157 | 2468 | 1931 | 1680 | 1297 | 2778 | 2171 | 1866 | 1436 | 3085 | 2424 | 2050 | 1575 | 3379 | 2677
1280 |  |  | 964 |  | 1568 |  | 1162 |  | 1898 |  | 1354 |  | 2225 |  | 1546 |  | 2547 |  | 1734 |  | 2867 |  | 1926 |  | 3185 |  | 2116 |  | 3488
1300 |  |  |  | 767 |  | 1225 |  | 919 |  | 1496 |  | 1067 |  | 1762 |  | 1213 |  | 2024 |  | 1360 |  | 2276 |  | 1505 |  | 2542 |  | 1651 |  | 2807
1320 |  |  | 994 |  | 1617 |  | 1199 |  | 1958 |  | 1397 |  | 2294 |  | 1595 |  | 2627 |  | 1789 |  | 2957 |  | 1987 |  | 3284 |  | 2182 |  | 3597
1360 |  |  | 1024 | 802 | 1666 | 1281 | 1235 | 962 | 2017 | 1565 | 1439 | 1117 | 2364 | 1843 | 1643 | 1269 | 2706 | 2118 | 1843 | 1423 | 3046 | 2381 | 2047 | 1575 | 3384 | 2659 | 2248 | 1727 | 3706 | 2936
1400 |  |  | 1054 |  | 1715 |  | 1271 |  | 2076 |  | 1481 |  | 2433 |  | 1691 |  | 2786 |  | 1897 |  | 3136 |  | 2107 |  | 3483 |  | 2314 |  | 3815
1420 |  |  |  | 838 |  | 1338 |  | 1004 |  | 1634 |  | 1166 |  | 1924 |  | 1325 |  | 2211 |  | 1485 |  | 2486 |  | 1644 |  | 2776 |  | 1803 |  | 3066
1440 |  |  | 1084 |  | 1764 |  | 1308 |  | 2136 |  | 1524 |  | 2503 |  | 1740 |  | 2866 |  | 1951 |  | 3226 |  | 2167 |  | 3583 |  | 2380 |  | 3924
1480 |  |  | 1114 | 873 | 1813 | 1394 | 1344 | 1046 | 2195 | 1703 | 1566 | 1215 | 2572 | 2005 | 1788 | 1381 | 2945 | 2304 | 2005 | 1548 | 3315 | 2591 | 2227 | 1714 | 3682 | 2893 | 2446 | 1880 | 4033 | 3195
1520 |  |  | 1145 |  | 1862 |  | 1380 |  | 2254 |  | 1608 |  | 2642 |  | 1836 |  | 3025 |  | 2060 |  | 3405 |  | 2288 |  | 3782 |  | 2513 |  | 4142
1540 |  |  |  | 909 |  | 1451 |  | 1089 |  | 1773 |  | 1264 |  | 2087 |  | 1437 |  | 2398 |  | 1611 |  | 2697 |  | 1783 |  | 3011 |  | 1956 |  | 3325
1560 |  |  | 1175 |  | 1911 |  | 1416 |  | 2313 |  | 1650 |  | 2711 |  | 1884 |  | 3104 |  | 2114 |  | 3494 |  | 2348 |  | 3881 |  | 2579 |  | 4251
1600 |  |  | 1205 | 944 | 1960 | 1507 | 1453 | 1131 | 2373 | 1842 | 1693 | 1314 | 2781 | 2168 | 1933 | 1493 | 3184 | 2491 | 2168 | 1674 | 3584 | 2802 | 2408 | 1853 | 3981 | 3128 | 2645 | 2032 | 4360 | 3454
1640 |  |  | 1235 |  | 2009 |  | 1489 |  | 2432 |  | 1735 |  | 2850 |  | 1981 |  | 3264 |  | 2222 |  | 3674 |  | 2468 |  | 4080 |  | 2711 |  | 4469
1660 |  |  |  | 979 |  | 1564 |  | 1174 |  | 1911 |  | 1363 |  | 2249 |  | 1549 |  | 2585 |  | 1736 |  | 2907 |  | 1922 |  | 3245 |  | 2108 |  | 3584
1680 |  |  | 1265 |  | 2058 |  | 1525 |  | 2491 |  | 1777 |  | 2920 |  | 2029 |  | 3343 |  | 2276 |  | 3763 |  | 2528 |  | 4180 |  | 2777 |  | 4578
1720 |  |  | 1295 | 1015 | 2107 | 1620 | 1562 | 1216 | 2551 | 1980 | 1820 | 1412 | 2989 | 2331 | 2078 | 1605 | 3423 | 2678 | 2331 | 1799 | 3853 | 3012 | 2589 | 1992 | 4279 | 3363 | 2843 | 2184 | 4687 | 3713
1760 |  |  | 1325 |  | 2156 |  | 1598 |  | 2610 |  | 1862 |  | 3059 |  | 2126 |  | 3502 |  | 2385 |  | 3942 |  | 2649 |  | 4379 |  | 2909 |  | 4796
1780 |  |  |  | 1050 |  | 1677 |  | 1258 |  | 2049 |  | 1461 |  | 2412 |  | 1661 |  | 2771 |  | 1862 |  | 3117 |  | 2061 |  | 3480 |  | 2261 |  | 3843
1800 |  |  | 1355 |  | 2205 |  | 1634 |  | 2669 |  | 1904 |  | 3128 |  | 2174 |  | 3582 |  | 2439 |  | 4032 |  | 2709 |  | 4478 |  | 2975 |  | 4905
1840 |  |  | 1386 | 1086 | 2254 | 1733 | 1671 | 1301 | 2729 | 2118 | 1947 | 1511 | 3198 | 2493 | 2223 | 1717 | 3662 | 2865 | 2493 | 1925 | 4122 | 3222 | 2769 | 2131 | 4578 | 3597 | 3042 | 2337 | 5014 | 3973
1880 |  |  | 1416 |  | 2303 |  | 1707 |  | 2788 |  | 1989 |  | 3267 |  | 2271 |  | 3741 |  | 2547 |  | 4211 |  | 2829 |  | 4677 |  | 3108 |  | 5123
1900 |  |  |  | 1121 |  | 1790 |  | 1343 |  | 2187 |  | 1560 |  | 2575 |  | 1773 |  | 2958 |  | 1987 |  | 3327 |  | 2200 |  | 3715 |  | 2413 |  | 4102
1920 |  |  | 1446 |  | 2352 |  | 1743 |  | 2847 |  | 2031 |  | 3337 |  | 2319 |  | 3821 |  | 2602 |  | 4301 |  | 2890 |  | 4777 |  | 3174 |  | 5232
1960 |  |  | 1476 | 1156 | 2401 | 1846 | 1780 | 1386 | 2907 | 2256 | 2074 | 1609 | 3406 | 2656 | 2368 | 1829 | 3900 | 3052 | 2656 | 2050 | 4390 | 3432 | 2950 | 2270 | 4876 | 3832 | 3240 | 2489 | 5341 | 4232
2000 |  |  | 1506 |  | 2450 |  | 1816 |  | 2966 |  | 2116 |  | 3476 |  | 2416 |  | 3980 |  | 2710 |  | 4480 |  | 3010 |  | 4976 |  | 3306 |  | 5450
2020 |  |  |  | 1192 |  | 1903 |  | 1428 |  | 2325 |  | 1658 |  | 2737 |  | 1885 |  | 3145 |  | 2113 |  | 3537 |  | 2339 |  | 3949 |  | 2565 |  | 4361
2040 |  |  | 1536 |  | 2499 |  | 1852 |  | 3025 |  | 2158 |  | 3546 |  | 2464 |  | 4060 |  | 2764 |  | 4570 |  | 3070 |  | 5076 |  | 3372 |  | 5559
2080 |  |  | 1566 | 1227 | 2548 | 1959 | 1889 | 1471 | 3085 | 2394 | 2201 | 1708 | 3615 | 2818 | 2513 | 1941 | 4139 | 3239 | 2818 | 2176 | 4659 | 3642 | 3130 | 2409 | 5175 | 4066 | 3438 | 2642 | 5668 | 4491
2120 |  |  | 1596 |  | 2597 |  | 1925 |  | 3144 |  | 2243 |  | 3685 |  | 2561 |  | 4219 |  | 2873 |  | 4749 |  | 3191 |  | 5275 |  | 3504 |  | 5777
2140 |  |  |  | 1263 |  | 2016 |  | 1513 |  | 2463 |  | 1757 |  | 2900 |  | 1997 |  | 3332 |  | 2238 |  | 3747 |  | 2478 |  | 4184 |  | 2718 |  | 4620
2160 |  |  | 1626 |  | 2646 |  | 1961 |  | 3203 |  | 2285 |  | 3754 |  | 2609 |  | 4298 |  | 2927 |  | 4838 |  | 3251 |  | 5374 |  | 3570 |  | 5886
2200 |  |  | 1657 | 1298 | 2695 | 2072 | 1998 | 1555 | 3263 | 2532 | 2328 | 1806 | 3824 | 2981 | 2658 | 2053 | 4378 | 3425 | 2981 | 2301 | 4928 | 3852 | 3311 | 2548 | 5474 | 4301 | 3637 | 2794 | 5995 | 4750
2240 |  |  | 1687 |  | 2744 |  | 2034 |  | 3322 |  | 2370 |  | 3893 |  | 2706 |  | 4458 |  | 3035 |  | 5018 |  | 3371 |  | 5573 |  | 3703 |  | 6104
2260 |  |  |  | 1333 |  | 2129 |  | 1598 |  | 2601 |  | 1855 |  | 3062 |  | 2109 |  | 3519 |  | 2364 |  | 3957 |  | 2617 |  | 4418 |  | 2870 |  | 4879
2280 |  |  | 1717 |  | 2793 |  | 2070 |  | 3381 |  | 2412 |  | 3963 |  | 2754 |  | 4537 |  | 3089 |  | 5107 |  | 3431 |  | 5673 |  | 3769 |  | 6213
2320 |  |  | 1747 | 1369 | 2842 | 2185 | 2107 | 1640 | 3441 | 2670 | 2455 | 1905 | 4032 | 3144 | 2803 | 2165 | 4617 | 3612 | 3144 | 2427 | 5197 | 4062 | 3492 | 2687 | 5772 | 4536 | 3835 | 2946 | 6322 | 5009
2360 |  |  | 1777 |  | 2891 |  | 2143 |  | 3500 |  | 2497 |  | 4102 |  | 2851 |  | 4696 |  | 3198 |  | 5286 |  | 3552 |  | 5872 |  | 3901 |  | 6431
2380 |  |  |  | 1404 |  | 2242 |  | 1683 |  | 2739 |  | 1954 |  | 3225 |  | 2221 |  | 3706 |  | 2489 |  | 4167 |  | 2756 |  | 4653 |  | 3023 |  | 5138
2400 |  |  | 1807 |  | 2940 |  | 2179 |  | 3559 |  | 2539 |  | 4171 |  | 2899 |  | 4776 |  | 3252 |  | 5376 |  | 3612 |  | 5971 |  | 3967 |  | 6540
2440 |  |  | 1837 | 1440 | 2989 | 2298 | 2216 | 1725 | 3619 | 2808 | 2582 | 2003 | 4241 | 3306 | 2948 | 2277 | 4856 | 3799 | 3306 | 2552 | 5466 | 4272 | 3672 | 2826 | 6071 | 4770 | 4033 | 3099 | 6649 | 5268
2480 |  |  | 1867 |  | 3038 |  | 2252 |  | 3678 |  | 2624 |  | 4310 |  | 2996 |  | 4935 |  | 3360 |  | 5555 |  | 3732 |  | 6170 |  | 4099 |  | 6758
2500 |  |  |  | 1475 |  | 2355 |  | 1768 |  | 2878 |  | 2053 |  | 3388 |  | 2333 |  | 3893 |  | 2615 |  | 4378 |  | 2895 |  | 4888 |  | 3175 |  | 5398
2520 |  |  | 1898 |  | 3087 |  | 2288 |  | 3737 |  | 2666 |  | 4380 |  | 3044 |  | 5015 |  | 3415 |  | 5645 |  | 3793 |  | 6270 |  | 4166 |  | 6867
2560 |  |  | 1928 | 1510 | 3136 | 2412 | 2324 | 1810 | 3796 | 2947 | 2708 | 2102 | 4449 | 3469 | 3092 | 2388 | 5094 | 3986 | 3469 | 2678 | 5734 | 4483 | 3853 | 2964 | 6369 | 5005 | 4232 | 3251 | 6976 | 5527
2600 |  |  | 1958 |  | 3185 |  | 2361 |  | 3856 |  | 2751 |  | 4519 |  | 3141 |  | 5174 |  | 3523 |  | 5824 |  | 3913 |  | 6469 |  | 4298 |  | 7085
2620 |  |  |  | 1546 |  | 2468 |  | 1852 |  | 3016 |  | 2151 |  | 3550 |  | 2444 |  | 4079 |  | 2741 |  | 4588 |  | 3034 |  | 5122 |  | 3327 |  | 5657
2640 |  |  | 1988 |  | 3234 |  | 2397 |  | 3915 |  | 2793 |  | 4588 |  | 3189 |  | 5254 |  | 3577 |  | 5914 |  | 3973 |  | 6568 |  | 4364 |  | 7194
2680 |  |  | 2018 | 1581 | 3283 | 2525 | 2433 | 1895 | 3974 | 3085 | 2835 | 2200 | 4658 | 3631 | 3237 | 2500 | 5333 | 4173 | 3631 | 2803 | 6003 | 4693 | 4033 | 3103 | 6668 | 5239 | 4430 | 3404 | 7303 | 5786
2720 |  |  | 2048 |  | 3332 |  | 2470 |  | 4034 |  | 2878 |  | 4727 |  | 3286 |  | 5413 |  | 3686 |  | 6093 |  | 4094 |  | 6767 |  | 4496 |  | 7412
2740 |  |  |  | 1617 |  | 2581 |  | 1937 |  | 3154 |  | 2250 |  | 3713 |  | 2556 |  | 4266 |  | 2866 |  | 4798 |  | 3173 |  | 5357 |  | 3480 |  | 5916
2760 |  |  | 2078 |  | 3381 |  | 2506 |  | 4093 |  | 2920 |  | 4797 |  | 3334 |  | 5492 |  | 3740 |  | 6182 |  | 4154 |  | 6867 |  | 4562 |  | 7521
2800 |  |  | 2108 | 1652 | 3430 | 2638 | 2542 | 1980 | 4152 | 3223 | 2962 | 2299 | 4866 | 3794 | 3382 | 2612 | 5572 | 4360 | 3794 | 2929 | 6272 | 4903 | 4214 | 3242 | 6966 | 5474 | 4628 | 3556 | 7630 | 6045
2840 |  |  | 2139 |  | 3479 |  | 2579 |  | 4212 |  | 3005 |  | 4936 |  | 3431 |  | 5652 |  | 3848 |  | 6362 |  | 4274 |  | 7066 |  | 4695 |  | 7739
2860 |  |  |  | 1687 |  | 2694 |  | 2022 |  | 3292 |  | 2348 |  | 3875 |  | 2668 |  | 4453 |  | 2992 |  | 5008 |  | 3312 |  | 5591 |  | 3632 |  | 6175
2880 |  |  | 2169 |  | 3528 |  | 2615 |  | 4271 |  | 3047 |  | 5005 |  | 3479 |  | 5731 |  | 3902 |  | 6451 |  | 4334 |  | 7165 |  | 4761 |  | 7848
2920 |  |  | 2199 | 1723 | 3577 | 2751 | 2651 | 2064 | 4330 | 3361 | 3089 | 2397 | 5075 | 3957 | 3527 | 2724 | 5811 | 4546 | 3957 | 3054 | 6541 | 5113 | 4395 | 3381 | 7265 | 5709 | 4827 | 3708 | 7957 | 6304
2960 |  |  | 2229 |  | 3626 |  | 2688 |  | 4390 |  | 3132 |  | 5144 |  | 3576 |  | 5890 |  | 4011 |  | 6630 |  | 4455 |  | 7364 |  | 4893 |  | 8066
2980 |  |  |  | 1758 |  | 2807 |  | 2107 |  | 3430 |  | 2447 |  | 4038 |  | 2780 |  | 4640 |  | 3117 |  | 5218 |  | 3451 |  | 5826 |  | 3785 |  | 6434
3000 |  |  | 2259 |  | 3675 |  | 2724 |  | 4449 |  | 3174 |  | 5214 |  | 3624 |  | 5970 |  | 4065 |  | 6720 |  | 4515 |  | 7464 |  | 4959 |  | 8175
Conversion to Logarithmic Outputs
Type |  |  | SCE (single) |  | SCD (double) |  | SCE (single) |  | SCD (double) |  | SCE (single) |  | SCD (double) |  | SCE (single) |  | SCD (double) |  | SCE (single) |  | SCD (double) |  | SCE (single) |  | SCD (double) |  | SCE (single) |  | SCD (double)
Height |  |  | 400 |  |  |  | 500 |  |  |  | 600 |  |  |  | 700 |  |  |  | 800 |  |  |  | 900 |  |  |  | 1000
Element spacing |  |  | 40 | 60 | 40 | 60 | 40 | 60 | 40 | 60 | 40 | 60 | 40 | 60 | 40 | 60 | 40 | 60 | 40 | 60 | 40 | 60 | 40 | 60 | 40 | 60 | 40 | 60 | 40 | 60
Length
400 |  |  | 301 | 236 | 490 | 377 | 363 | 283 | 593 | 460 | 423 | 328 | 695 | 542 | 483 | 373 | 796 | 623 | 542 | 418 | 896 | 700 | 602 | 463 | 995 | 782 | 661 | 508 | 1090 | 864
440 |  |  | 331 |  | 539 |  | 400 |  | 653 |  | 466 |  | 765 |  | 532 |  | 876 |  | 596 |  | 986 |  | 662 |  | 1095 |  | 727 |  | 1199
460 |  |  |  | 271 |  | 433 |  | 325 |  | 529 |  | 378 |  | 623 |  | 429 |  | 716 |  | 481 |  | 805 |  | 533 |  | 899 |  | 584 |  | 993
480 |  |  | 361 |  | 588 |  | 436 |  | 712 |  | 508 |  | 834 |  | 580 |  | 955 |  | 650 |  | 1075 |  | 722 |  | 1194 |  | 793 |  | 1308
520 |  |  | 392 | 307 | 637 | 490 | 472 | 368 | 771 | 599 | 550 | 427 | 904 | 705 | 628 | 485 | 1035 | 810 | 705 | 544 | 1165 | 911 | 783 | 602 | 1294 | 1017 | 860 | 660 | 1417 | 1123
560 |  |  | 422 |  | 686 |  | 508 |  | 830 |  | 592 |  | 973 |  | 676 |  | 1114 |  | 759 |  | 1254 |  | 843 |  | 1393 |  | 926 |  | 1526
580 |  |  |  | 342 |  | 546 |  | 410 |  | 668 |  | 476 |  | 786 |  | 541 |  | 903 |  | 607 |  | 1016 |  | 672 |  | 1134 |  | 737 |  | 1252
600 |  |  | 452 |  | 735 |  | 545 |  | 890 |  | 635 |  | 1043 |  | 725 | 560 | 1194 | 934 | 813 |  | 1344 |  | 903 | 695 | 1493 |  | 992 |  | 1635
640 |  |  | 482 | 378 | 784 | 603 | 581 | 452 | 949 | 737 | 677 | 525 | 1112 | 867 | 773 | 597 | 1274 | 996 | 867 | 669 | 1434 | 1121 | 963 |  | 1592 | 1251 | 1058 | 813 | 1744 | 1382
680 |  |  | 512 |  | 833 |  | 617 |  | 1008 |  | 719 |  | 1182 |  | 821 |  | 1353 |  | 921 |  | 1523 |  | 1023 | 787 | 1692 |  | 1124 |  | 1853
700 |  |  |  | 413 |  | 659 |  | 495 |  | 806 |  | 575 |  | 949 |  | 653 |  | 1090 |  | 732 |  | 1226 |  | 811 |  | 1369 |  | 889 |  | 1511
720 |  |  | 542 |  | 882 |  | 654 |  | 1068 |  | 762 |  | 1251 |  | 870 |  | 1433 |  | 976 |  | 1613 |  | 1084 |  | 1791 |  | 1190 |  | 1962
760 |  |  | 572 | 448 | 931 | 716 | 690 | 537 | 1127 | 875 | 804 | 624 | 1321 | 1030 | 918 | 709 | 1512 | 1183 | 1030 | 795 | 1702 | 1331 | 1144 | 880 | 1891 | 1486 | 1256 | 965 | 2071 | 1641
800 |  |  | 602 |  | 980 |  | 726 |  | 1186 |  | 846 |  | 1390 |  | 966 |  | 1592 |  | 1084 |  | 1792 |  | 1204 |  | 1990 |  | 1322 |  | 2180
820 |  |  |  | 484 |  | 772 |  | 580 |  | 944 |  | 673 |  | 1111 |  | 765 |  | 1277 |  | 858 |  | 1436 |  | 950 |  | 1603 |  | 1041 |  | 1770
840 |  |  | 633 |  | 1029 |  | 763 |  | 1246 |  | 889 |  | 1460 |  | 1015 |  | 1672 |  | 1138 |  | 1882 |  | 1264 |  | 2090 |  | 1389 |  | 2289
880 |  |  | 663 | 519 | 1078 | 829 | 799 | 622 | 1305 | 1013 | 931 | 722 | 1529 | 1192 | 1063 | 821 | 1751 | 1370 | 1192 | 920 | 1971 | 1541 | 1324 | 1019 | 2189 | 1720 | 1455 | 1118 | 2398 | 1900
920 |  |  | 693 |  | 1127 |  | 835 |  | 1364 |  | 973 |  | 1599 |  | 1111 |  | 1831 |  | 1247 |  | 2061 |  | 1385 |  | 2289 |  | 1521 |  | 2507
940 |  |  |  | 555 |  | 885 |  | 665 |  | 1082 |  | 772 |  | 1274 |  | 877 |  | 1464 |  | 983 |  | 1646 |  | 1089 |  | 1838 |  | 1194 |  | 2029
960 |  |  | 723 |  | 1176 |  | 872 |  | 1424 |  | 1016 |  | 1668 |  | 1160 |  | 1910 |  | 1301 |  | 2150 |  | 1445 |  | 2388 |  | 1587 |  | 2616
1000 |  |  | 753 | 590 | 1225 | 942 | 908 | 707 | 1483 | 1151 | 1058 | 821 | 1738 | 1355 | 1208 | 933 | 1990 | 1557 | 1355 | 1046 | 2240 | 1751 | 1505 | 1158 | 2488 | 1955 | 1653 | 1270 | 2725 | 2159
1040 |  |  | 783 |  | 1274 |  | 944 |  | 1542 |  | 1100 |  | 1808 |  | 1256 |  | 2070 |  | 1409 |  | 2330 |  | 1565 |  | 2588 |  | 1719 |  | 2834
1060 |  |  |  | 625 |  | 999 |  | 749 |  | 1220 |  | 870 |  | 1436 |  | 989 |  | 1650 |  | 1109 |  | 1856 |  | 1227 |  | 2072 |  | 1346 |  | 2289
1080 |  |  | 813 |  | 1323 |  | 981 |  | 1602 |  | 1143 |  | 1877 |  | 1305 |  | 2149 |  | 1463 |  | 2419 |  | 1625 |  | 2687 |  | 1785 |  | 2943
1120 |  |  | 843 | 661 | 1372 | 1055 | 1017 | 792 | 1661 | 1289 | 1185 | 920 | 1947 | 1518 | 1353 | 1045 | 2229 | 1744 | 1518 | 1172 | 2509 | 1961 | 1686 | 1297 | 2787 | 2190 | 1851 | 1422 | 3052 | 2418
1160 |  |  | 873 |  | 1421 |  | 1053 |  | 1720 |  | 1227 |  | 2016 |  | 1401 |  | 2308 |  | 1572 |  | 2598 |  | 1746 |  | 2886 |  | 1917 |  | 3161
1180 |  |  |  | 696 |  | 1112 |  | 834 |  | 1358 |  | 969 |  | 1599 |  | 1101 |  | 1837 |  | 1234 |  | 2066 |  | 1366 |  | 2307 |  | 1499 |  | 2548
1200 |  |  | 904 |  | 1470 |  | 1090 |  | 1780 |  | 1270 |  | 2086 |  | 1450 |  | 2388 |  | 1626 |  | 2688 |  | 1806 |  | 2986 |  | 1984 |  | 3270
1240 |  |  | 934 | 732 | 1519 | 1168 | 1126 | 877 | 1839 | 1427 | 1312 | 1018 | 2155 | 1680 | 1498 | 1157 | 2468 | 1931 | 1680 | 1297 | 2778 | 2171 | 1866 | 1436 | 3085 | 2424 | 2050 | 1575 | 3379 | 2677
1280 |  |  | 964 |  | 1568 |  | 1162 |  | 1898 |  | 1354 |  | 2225 |  | 1546 |  | 2547 |  | 1734 |  | 2867 |  | 1926 |  | 3185 |  | 2116 |  | 3488
1300 |  |  |  | 767 |  | 1225 |  | 919 |  | 1496 |  | 1067 |  | 1762 |  | 1213 |  | 2024 |  | 1360 |  | 2276 |  | 1505 |  | 2542 |  | 1651 |  | 2807
1320 |  |  | 994 |  | 1617 |  | 1199 |  | 1958 |  | 1397 |  | 2294 |  | 1595 |  | 2627 |  | 1789 |  | 2957 |  | 1987 |  | 3284 |  | 2182 |  | 3597
1360 |  |  | 1024 | 802 | 1666 | 1281 | 1235 | 962 | 2017 | 1565 | 1439 | 1117 | 2364 | 1843 | 1643 | 1269 | 2706 | 2118 | 1843 | 1423 | 3046 | 2381 | 2047 | 1575 | 3384 | 2659 | 2248 | 1727 | 3706 | 2936
1400 |  |  | 1054 |  | 1715 |  | 1271 |  | 2076 |  | 1481 |  | 2433 |  | 1691 |  | 2786 |  | 1897 |  | 3136 |  | 2107 |  | 3483 |  | 2314 |  | 3815
1420 |  |  |  | 838 |  | 1338 |  | 1004 |  | 1634 |  | 1166 |  | 1924 |  | 1325 |  | 2211 |  | 1485 |  | 2486 |  | 1644 |  | 2776 |  | 1803 |  | 3066
1440 |  |  | 1084 |  | 1764 |  | 1308 |  | 2136 |  | 1524 |  | 2503 |  | 1740 |  | 2866 |  | 1951 |  | 3226 |  | 2167 |  | 3583 |  | 2380 |  | 3924
1480 |  |  | 1114 | 873 | 1813 | 1394 | 1344 | 1046 | 2195 | 1703 | 1566 | 1215 | 2572 | 2005 | 1788 | 1381 | 2945 | 2304 | 2005 | 1548 | 3315 | 2591 | 2227 | 1714 | 3682 | 2893 | 2446 | 1880 | 4033 | 3195
1520 |  |  | 1145 |  | 1862 |  | 1380 |  | 2254 |  | 1608 |  | 2642 |  | 1836 |  | 3025 |  | 2060 |  | 3405 |  | 2288 |  | 3782 |  | 2513 |  | 4142
1540 |  |  |  | 909 |  | 1451 |  | 1089 |  | 1773 |  | 1264 |  | 2087 |  | 1437 |  | 2398 |  | 1611 |  | 2697 |  | 1783 |  | 3011 |  | 1956 |  | 3325
1560 |  |  | 1175 |  | 1911 |  | 1416 |  | 2313 |  | 1650 |  | 2711 |  | 1884 |  | 3104 |  | 2114 |  | 3494 |  | 2348 |  | 3881 |  | 2579 |  | 4251
1600 |  |  | 1205 | 944 | 1960 | 1507 | 1453 | 1131 | 2373 | 1842 | 1693 | 1314 | 2781 | 2168 | 1933 | 1493 | 3184 | 2491 | 2168 | 1674 | 3584 | 2802 | 2408 | 1853 | 3981 | 3128 | 2645 | 2032 | 4360 | 3454
1640 |  |  | 1235 |  | 2009 |  | 1489 |  | 2432 |  | 1735 |  | 2850 |  | 1981 |  | 3264 |  | 2222 |  | 3674 |  | 2468 |  | 4080 |  | 2711 |  | 4469
1660 |  |  |  | 979 |  | 1564 |  | 1174 |  | 1911 |  | 1363 |  | 2249 |  | 1549 |  | 2585 |  | 1736 |  | 2907 |  | 1922 |  | 3245 |  | 2108 |  | 3584
1680 |  |  | 1265 |  | 2058 |  | 1525 |  | 2491 |  | 1777 |  | 2920 |  | 2029 |  | 3343 |  | 2276 |  | 3763 |  | 2528 |  | 4180 |  | 2777 |  | 4578
1720 |  |  | 1295 | 1015 | 2107 | 1620 | 1562 | 1216 | 2551 | 1980 | 1820 | 1412 | 2989 | 2331 | 2078 | 1605 | 3423 | 2678 | 2331 | 1799 | 3853 | 3012 | 2589 | 1992 | 4279 | 3363 | 2843 | 2184 | 4687 | 3713
1760 |  |  | 1325 |  | 2156 |  | 1598 |  | 2610 |  | 1862 |  | 3059 |  | 2126 |  | 3502 |  | 2385 |  | 3942 |  | 2649 |  | 4379 |  | 2909 |  | 4796
1780 |  |  |  | 1050 |  | 1677 |  | 1258 |  | 2049 |  | 1461 |  | 2412 |  | 1661 |  | 2771 |  | 1862 |  | 3117 |  | 2061 |  | 3480 |  | 2261 |  | 3843
1800 |  |  | 1355 |  | 2205 |  | 1634 |  | 2669 |  | 1904 |  | 3128 |  | 2174 |  | 3582 |  | 2439 |  | 4032 |  | 2709 |  | 4478 |  | 2975 |  | 4905
1840 |  |  | 1386 | 1086 | 2254 | 1733 | 1671 | 1301 | 2729 | 2118 | 1947 | 1511 | 3198 | 2493 | 2223 | 1717 | 3662 | 2865 | 2493 | 1925 | 4122 | 3222 | 2769 | 2131 | 4578 | 3597 | 3042 | 2337 | 5014 | 3973
1880 |  |  | 1416 |  | 2303 |  | 1707 |  | 2788 |  | 1989 |  | 3267 |  | 2271 |  | 3741 |  | 2547 |  | 4211 |  | 2829 |  | 4677 |  | 3108 |  | 5123
1900 |  |  |  | 1121 |  | 1790 |  | 1343 |  | 2187 |  | 1560 |  | 2575 |  | 1773 |  | 2958 |  | 1987 |  | 3327 |  | 2200 |  | 3715 |  | 2413 |  | 4102
1920 |  |  | 1446 |  | 2352 |  | 1743 |  | 2847 |  | 2031 |  | 3337 |  | 2319 |  | 3821 |  | 2602 |  | 4301 |  | 2890 |  | 4777 |  | 3174 |  | 5232
1960 |  |  | 1476 | 1156 | 2401 | 1846 | 1780 | 1386 | 2907 | 2256 | 2074 | 1609 | 3406 | 2656 | 2368 | 1829 | 3900 | 3052 | 2656 | 2050 | 4390 | 3432 | 2950 | 2270 | 4876 | 3832 | 3240 | 2489 | 5341 | 4232
2000 |  |  | 1506 |  | 2450 |  | 1816 |  | 2966 |  | 2116 |  | 3476 |  | 2416 |  | 3980 |  | 2710 |  | 4480 |  | 3010 |  | 4976 |  | 3306 |  | 5450
2020 |  |  |  | 1192 |  | 1903 |  | 1428 |  | 2325 |  | 1658 |  | 2737 |  | 1885 |  | 3145 |  | 2113 |  | 3537 |  | 2339 |  | 3949 |  | 2565 |  | 4361
2040 |  |  | 1536 |  | 2499 |  | 1852 |  | 3025 |  | 2158 |  | 3546 |  | 2464 |  | 4060 |  | 2764 |  | 4570 |  | 3070 |  | 5076 |  | 3372 |  | 5559
2080 |  |  | 1566 | 1227 | 2548 | 1959 | 1889 | 1471 | 3085 | 2394 | 2201 | 1708 | 3615 | 2818 | 2513 | 1941 | 4139 | 3239 | 2818 | 2176 | 4659 | 3642 | 3130 | 2409 | 5175 | 4066 | 3438 | 2642 | 5668 | 4491
2120 |  |  | 1596 |  | 2597 |  | 1925 |  | 3144 |  | 2243 |  | 3685 |  | 2561 |  | 4219 |  | 2873 |  | 4749 |  | 3191 |  | 5275 |  | 3504 |  | 5777
2140 |  |  |  | 1263 |  | 2016 |  | 1513 |  | 2463 |  | 1757 |  | 2900 |  | 1997 |  | 3332 |  | 2238 |  | 3747 |  | 2478 |  | 4184 |  | 2718 |  | 4620
2160 |  |  | 1626 |  | 2646 |  | 1961 |  | 3203 |  | 2285 |  | 3754 |  | 2609 |  | 4298 |  | 2927 |  | 4838 |  | 3251 |  | 5374 |  | 3570 |  | 5886
2200 |  |  | 1657 | 1298 | 2695 | 2072 | 1998 | 1555 | 3263 | 2532 | 2328 | 1806 | 3824 | 2981 | 2658 | 2053 | 4378 | 3425 | 2981 | 2301 | 4928 | 3852 | 3311 | 2548 | 5474 | 4301 | 3637 | 2794 | 5995 | 4750
2240 |  |  | 1687 |  | 2744 |  | 2034 |  | 3322 |  | 2370 |  | 3893 |  | 2706 |  | 4458 |  | 3035 |  | 5018 |  | 3371 |  | 5573 |  | 3703 |  | 6104
2260 |  |  |  | 1333 |  | 2129 |  | 1598 |  | 2601 |  | 1855 |  | 3062 |  | 2109 |  | 3519 |  | 2364 |  | 3957 |  | 2617 |  | 4418 |  | 2870 |  | 4879
2280 |  |  | 1717 |  | 2793 |  | 2070 |  | 3381 |  | 2412 |  | 3963 |  | 2754 |  | 4537 |  | 3089 |  | 5107 |  | 3431 |  | 5673 |  | 3769 |  | 6213
2320 |  |  | 1747 | 1369 | 2842 | 2185 | 2107 | 1640 | 3441 | 2670 | 2455 | 1905 | 4032 | 3144 | 2803 | 2165 | 4617 | 3612 | 3144 | 2427 | 5197 | 4062 | 3492 | 2687 | 5772 | 4536 | 3835 | 2946 | 6322 | 5009
2360 |  |  | 1777 |  | 2891 |  | 2143 |  | 3500 |  | 2497 |  | 4102 |  | 2851 |  | 4696 |  | 3198 |  | 5286 |  | 3552 |  | 5872 |  | 3901 |  | 6431
2380 |  |  |  | 1404 |  | 2242 |  | 1683 |  | 2739 |  | 1954 |  | 3225 |  | 2221 |  | 3706 |  | 2489 |  | 4167 |  | 2756 |  | 4653 |  | 3023 |  | 5138
2400 |  |  | 1807 |  | 2940 |  | 2179 |  | 3559 |  | 2539 |  | 4171 |  | 2899 |  | 4776 |  | 3252 |  | 5376 |  | 3612 |  | 5971 |  | 3967 |  | 6540
2440 |  |  | 1837 | 1440 | 2989 | 2298 | 2216 | 1725 | 3619 | 2808 | 2582 | 2003 | 4241 | 3306 | 2948 | 2277 | 4856 | 3799 | 3306 | 2552 | 5466 | 4272 | 3672 | 2826 | 6071 | 4770 | 4033 | 3099 | 6649 | 5268
2480 |  |  | 1867 |  | 3038 |  | 2252 |  | 3678 |  | 2624 |  | 4310 |  | 2996 |  | 4935 |  | 3360 |  | 5555 |  | 3732 |  | 6170 |  | 4099 |  | 6758
2500 |  |  |  | 1475 |  | 2355 |  | 1768 |  | 2878 |  | 2053 |  | 3388 |  | 2333 |  | 3893 |  | 2615 |  | 4378 |  | 2895 |  | 4888 |  | 3175 |  | 5398
2520 |  |  | 1898 |  | 3087 |  | 2288 |  | 3737 |  | 2666 |  | 4380 |  | 3044 |  | 5015 |  | 3415 |  | 5645 |  | 3793 |  | 6270 |  | 4166 |  | 6867
2560 |  |  | 1928 | 1510 | 3136 | 2412 | 2324 | 1810 | 3796 | 2947 | 2708 | 2102 | 4449 | 3469 | 3092 | 2388 | 5094 | 3986 | 3469 | 2678 | 5734 | 4483 | 3853 | 2964 | 6369 | 5005 | 4232 | 3251 | 6976 | 5527
2600 |  |  | 1958 |  | 3185 |  | 2361 |  | 3856 |  | 2751 |  | 4519 |  | 3141 |  | 5174 |  | 3523 |  | 5824 |  | 3913 |  | 6469 |  | 4298 |  | 7085
2620 |  |  |  | 1546 |  | 2468 |  | 1852 |  | 3016 |  | 2151 |  | 3550 |  | 2444 |  | 4079 |  | 2741 |  | 4588 |  | 3034 |  | 5122 |  | 3327 |  | 5657
2640 |  |  | 1988 |  | 3234 |  | 2397 |  | 3915 |  | 2793 |  | 4588 |  | 3189 |  | 5254 |  | 3577 |  | 5914 |  | 3973 |  | 6568 |  | 4364 |  | 7194
2680 |  |  | 2018 | 1581 | 3283 | 2525 | 2433 | 1895 | 3974 | 3085 | 2835 | 2200 | 4658 | 3631 | 3237 | 2500 | 5333 | 4173 | 3631 | 2803 | 6003 | 4693 | 4033 | 3103 | 6668 | 5239 | 4430 | 3404 | 7303 | 5786
2720 |  |  | 2048 |  | 3332 |  | 2470 |  | 4034 |  | 2878 |  | 4727 |  | 3286 |  | 5413 |  | 3686 |  | 6093 |  | 4094 |  | 6767 |  | 4496 |  | 7412
2740 |  |  |  | 1617 |  | 2581 |  | 1937 |  | 3154 |  | 2250 |  | 3713 |  | 2556 |  | 4266 |  | 2866 |  | 4798 |  | 3173 |  | 5357 |  | 3480 |  | 5916
2760 |  |  | 2078 |  | 3381 |  | 2506 |  | 4093 |  | 2920 |  | 4797 |  | 3334 |  | 5492 |  | 3740 |  | 6182 |  | 4154 |  | 6867 |  | 4562 |  | 7521
2800 |  |  | 2108 | 1652 | 3430 | 2638 | 2542 | 1980 | 4152 | 3223 | 2962 | 2299 | 4866 | 3794 | 3382 | 2612 | 5572 | 4360 | 3794 | 2929 | 6272 | 4903 | 4214 | 3242 | 6966 | 5474 | 4628 | 3556 | 7630 | 6045
2840 |  |  | 2139 |  | 3479 |  | 2579 |  | 4212 |  | 3005 |  | 4936 |  | 3431 |  | 5652 |  | 3848 |  | 6362 |  | 4274 |  | 7066 |  | 4695 |  | 7739
2860 |  |  |  | 1687 |  | 2694 |  | 2022 |  | 3292 |  | 2348 |  | 3875 |  | 2668 |  | 4453 |  | 2992 |  | 5008 |  | 3312 |  | 5591 |  | 3632 |  | 6175
2880 |  |  | 2169 |  | 3528 |  | 2615 |  | 4271 |  | 3047 |  | 5005 |  | 3479 |  | 5731 |  | 3902 |  | 6451 |  | 4334 |  | 7165 |  | 4761 |  | 7848
2920 |  |  | 2199 | 1723 | 3577 | 2751 | 2651 | 2064 | 4330 | 3361 | 3089 | 2397 | 5075 | 3957 | 3527 | 2724 | 5811 | 4546 | 3957 | 3054 | 6541 | 5113 | 4395 | 3381 | 7265 | 5709 | 4827 | 3708 | 7957 | 6304
2960 |  |  | 2229 |  | 3626 |  | 2688 |  | 4390 |  | 3132 |  | 5144 |  | 3576 |  | 5890 |  | 4011 |  | 6630 |  | 4455 |  | 7364 |  | 4893 |  | 8066
2980 |  |  |  | 1758 |  | 2807 |  | 2107 |  | 3430 |  | 2447 |  | 4038 |  | 2780 |  | 4640 |  | 3117 |  | 5218 |  | 3451 |  | 5826 |  | 3785 |  | 6434
3000 |  |  | 2259 |  | 3675 |  | 2724 |  | 4449 |  | 3174 |  | 5214 |  | 3624 |  | 5970 |  | 4065 |  | 6720 |  | 4515 |  | 7464 |  | 4959 |  | 8175
Conversion to Btu/hr
Type |  |  | SCE (single) |  | SCD (double) |  | SCE (single) |  | SCD (double) |  | SCE (single) |  | SCD (double) |  | SCE (single) |  | SCD (double) |  | SCE (single) |  | SCD (double) |  | SCE (single) |  | SCD (double) |  | SCE (single) |  | SCD (double)
Height |  |  | 400 |  |  |  | 500 |  |  |  | 600 |  |  |  | 700 |  |  |  | 800 |  |  |  | 900 |  |  |  | 1000
Element spacing |  |  | 40 | 60 | 40 | 60 | 40 | 60 | 40 | 60 | 40 | 60 | 40 | 60 | 40 | 60 | 40 | 60 | 40 | 60 | 40 | 60 | 40 | 60 | 40 | 60 | 40 | 60 | 40 | 60
Length
400 |  |  | 1027.012 | 805.232 | 1671.88 | 1286.324 | 1238.556 | 965.596 | 2023.316 | 1569.52 | 1443.276 | 1119.136 | 2371.34 | 1849.304 | 1647.996 | 1272.676 | 2715.952 | 2125.676 | 1849.304 | 1426.216 | 3057.152 | 2388.4 | 2054.024 | 1579.756 | 3394.94 | 2668.184 | 2255.332 | 1733.296 | 3719.08 | 2947.968
440 |  |  | 1129.372 |  | 1839.068 |  | 1364.8 |  | 2228.036 |  | 1589.992 |  | 2610.18 |  | 1815.184 |  | 2988.912 |  | 2033.552 |  | 3364.232 |  | 2258.744 |  | 3736.14 |  | 2480.524 |  | 4090.988
460 |  |  |  | 924.652 |  | 1477.396 |  | 1108.9 |  | 1804.948 |  | 1289.736 |  | 2125.676 |  | 1463.748 |  | 2442.992 |  | 1641.172 |  | 2746.66 |  | 1818.596 |  | 3067.388 |  | 1992.608 |  | 3388.116
480 |  |  | 1231.732 |  | 2006.256 |  | 1487.632 |  | 2429.344 |  | 1733.296 |  | 2845.608 |  | 1978.96 |  | 3258.46 |  | 2217.8 |  | 3667.9 |  | 2463.464 |  | 4073.928 |  | 2705.716 |  | 4462.896
520 |  |  | 1337.504 | 1047.484 | 2173.444 | 1671.88 | 1610.464 | 1255.616 | 2630.652 | 2043.788 | 1876.6 | 1456.924 | 3084.448 | 2405.46 | 2142.736 | 1654.82 | 3531.42 | 2763.72 | 2405.46 | 1856.128 | 3974.98 | 3108.332 | 2671.596 | 2054.024 | 4415.128 | 3470.004 | 2934.32 | 2251.92 | 4834.804 | 3831.676
560 |  |  | 1439.864 |  | 2340.632 |  | 1733.296 |  | 2831.96 |  | 2019.904 |  | 3319.876 |  | 2306.512 |  | 3800.968 |  | 2589.708 |  | 4278.648 |  | 2876.316 |  | 4752.916 |  | 3159.512 |  | 5206.712
580 |  |  |  | 1166.904 |  | 1862.952 |  | 1398.92 |  | 2279.216 |  | 1624.112 |  | 2681.832 |  | 1845.892 |  | 3081.036 |  | 2071.084 |  | 3466.592 |  | 2292.864 |  | 3869.208 |  | 2514.644 |  | 4271.824
600 |  |  | 1542.224 |  | 2507.82 |  | 1859.54 |  | 3036.68 |  | 2166.62 |  | 3558.716 |  | 2473.7 |  | 4073.928 |  | 2773.956 |  | 4585.728 |  | 3081.036 |  | 5094.116 |  | 3384.704 |  | 5578.62
640 |  |  | 1644.584 | 1289.736 | 2675.008 | 2057.436 | 1982.372 | 1542.224 | 3237.988 | 2514.644 | 2309.924 | 1791.3 | 3794.144 | 2958.204 | 2637.476 | 2036.964 | 4346.888 | 3398.352 | 2958.204 | 2282.628 | 4892.808 | 3824.852 | 3285.756 | 2528.292 | 5431.904 | 4268.412 | 3609.896 | 2773.956 | 5950.528 | 4715.384
680 |  |  | 1746.944 |  | 2842.196 |  | 2105.204 |  | 3439.296 |  | 2453.228 |  | 4032.984 |  | 2801.252 |  | 4616.436 |  | 3142.452 |  | 5196.476 |  | 3490.476 |  | 5773.104 |  | 3835.088 |  | 6322.436
700 |  |  |  | 1409.156 |  | 2248.508 |  | 1688.94 |  | 2750.072 |  | 1961.9 |  | 3237.988 |  | 2228.036 |  | 3719.08 |  | 2497.584 |  | 4183.112 |  | 2767.132 |  | 4671.028 |  | 3033.268 |  | 5155.532
720 |  |  | 1849.304 |  | 3009.384 |  | 2231.448 |  | 3644.016 |  | 2599.944 |  | 4268.412 |  | 2968.44 |  | 4889.396 |  | 3330.112 |  | 5503.556 |  | 3698.608 |  | 6110.892 |  | 4060.28 |  | 6694.344
760 |  |  | 1951.664 | 1528.576 | 3176.572 | 2442.992 | 2354.28 | 1832.244 | 3845.324 | 2985.5 | 2743.248 | 2129.088 | 4507.252 | 3514.36 | 3132.216 | 2419.108 | 5158.944 | 4036.396 | 3514.36 | 2712.54 | 5807.224 | 4541.372 | 3903.328 | 3002.56 | 6452.092 | 5070.232 | 4285.472 | 3292.58 | 7066.252 | 5599.092
800 |  |  | 2054.024 |  | 3343.76 |  | 2477.112 |  | 4046.632 |  | 2886.552 |  | 4742.68 |  | 3295.992 |  | 5431.904 |  | 3698.608 |  | 6114.304 |  | 4108.048 |  | 6789.88 |  | 4510.664 |  | 7438.16
820 |  |  |  | 1651.408 |  | 2634.064 |  | 1978.96 |  | 3220.928 |  | 2296.276 |  | 3790.732 |  | 2610.18 |  | 4357.124 |  | 2927.496 |  | 4899.632 |  | 3241.4 |  | 5469.436 |  | 3551.892 |  | 6039.24
840 |  |  | 2159.796 |  | 3510.948 |  | 2603.356 |  | 4251.352 |  | 3033.268 |  | 4981.52 |  | 3463.18 |  | 5704.864 |  | 3882.856 |  | 6421.384 |  | 4312.768 |  | 7131.08 |  | 4739.268 |  | 7810.068
880 |  |  | 2262.156 | 1770.828 | 3678.136 | 2828.548 | 2726.188 | 2122.264 | 4452.66 | 3456.356 | 3176.572 | 2463.464 | 5216.948 | 4067.104 | 3626.956 | 2801.252 | 5974.412 | 4674.44 | 4067.104 | 3139.04 | 6725.052 | 5257.892 | 4517.488 | 3476.828 | 7468.868 | 5868.64 | 4964.46 | 3814.616 | 8181.976 | 6482.8
920 |  |  | 2364.516 |  | 3845.324 |  | 2849.02 |  | 4653.968 |  | 3319.876 |  | 5455.788 |  | 3790.732 |  | 6247.372 |  | 4254.764 |  | 7032.132 |  | 4725.62 |  | 7810.068 |  | 5189.652 |  | 8553.884
940 |  |  |  | 1893.66 |  | 3019.62 |  | 2268.98 |  | 3691.784 |  | 2634.064 |  | 4346.888 |  | 2992.324 |  | 4995.168 |  | 3353.996 |  | 5616.152 |  | 3715.668 |  | 6271.256 |  | 4073.928 |  | 6922.948
960 |  |  | 2466.876 |  | 4012.512 |  | 2975.264 |  | 4858.688 |  | 3466.592 |  | 5691.216 |  | 3957.92 |  | 6516.92 |  | 4439.012 |  | 7335.8 |  | 4930.34 |  | 8147.856 |  | 5414.844 |  | 8925.792
1000 |  |  | 2569.236 | 2013.08 | 4179.7 | 3214.104 | 3098.096 | 2412.284 | 5059.996 | 3927.212 | 3609.896 | 2801.252 | 5930.056 | 4623.26 | 4121.696 | 3183.396 | 6789.88 | 5312.484 | 4623.26 | 3568.952 | 7642.88 | 5974.412 | 5135.06 | 3951.096 | 8489.056 | 6670.46 | 5640.036 | 4333.24 | 9297.7 | 7366.508
1040 |  |  | 2671.596 |  | 4346.888 |  | 3220.928 |  | 5261.304 |  | 3753.2 |  | 6168.896 |  | 4285.472 |  | 7062.84 |  | 4807.508 |  | 7949.96 |  | 5339.78 |  | 8830.256 |  | 5865.228 |  | 9669.608
1060 |  |  |  | 2132.5 |  | 3408.588 |  | 2555.588 |  | 4162.64 |  | 2968.44 |  | 4899.632 |  | 3374.468 |  | 5629.8 |  | 3783.908 |  | 6332.672 |  | 4186.524 |  | 7069.664 |  | 4592.552 |  | 7810.068
1080 |  |  | 2773.956 |  | 4514.076 |  | 3347.172 |  | 5466.024 |  | 3899.916 |  | 6404.324 |  | 4452.66 |  | 7332.388 |  | 4991.756 |  | 8253.628 |  | 5544.5 |  | 9168.044 |  | 6090.42 |  | 10041.516
1120 |  |  | 2876.316 | 2255.332 | 4681.264 | 3599.66 | 3470.004 | 2702.304 | 5667.332 | 4398.068 | 4043.22 | 3139.04 | 6643.164 | 5179.416 | 4616.436 | 3565.54 | 7605.348 | 5950.528 | 5179.416 | 3998.864 | 8560.708 | 6690.932 | 5752.632 | 4425.364 | 9509.244 | 7472.28 | 6315.612 | 4851.864 | 10413.424 | 8250.216
1160 |  |  | 2978.676 |  | 4848.452 |  | 3592.836 |  | 5868.64 |  | 4186.524 |  | 6878.592 |  | 4780.212 |  | 7874.896 |  | 5363.664 |  | 8864.376 |  | 5957.352 |  | 9847.032 |  | 6540.804 |  | 10785.332
1180 |  |  |  | 2374.752 |  | 3794.144 |  | 2845.608 |  | 4633.496 |  | 3306.228 |  | 5455.788 |  | 3756.612 |  | 6267.844 |  | 4210.408 |  | 7049.192 |  | 4660.792 |  | 7871.484 |  | 5114.588 |  | 8693.776
1200 |  |  | 3084.448 |  | 5015.64 |  | 3719.08 |  | 6073.36 |  | 4333.24 |  | 7117.432 |  | 4947.4 |  | 8147.856 |  | 5547.912 |  | 9171.456 |  | 6162.072 |  | 10188.232 |  | 6769.408 |  | 11157.24
1240 |  |  | 3186.808 | 2497.584 | 5182.828 | 3985.216 | 3841.912 | 2992.324 | 6274.668 | 4868.924 | 4476.544 | 3473.416 | 7352.86 | 5732.16 | 5111.176 | 3947.684 | 8420.816 | 6588.572 | 5732.16 | 4425.364 | 9478.536 | 7407.452 | 6366.792 | 4899.632 | 10526.02 | 8270.688 | 6994.6 | 5373.9 | 11529.148 | 9133.924
1280 |  |  | 3289.168 |  | 5350.016 |  | 3964.744 |  | 6475.976 |  | 4619.848 |  | 7591.7 |  | 5274.952 |  | 8690.364 |  | 5916.408 |  | 9782.204 |  | 6571.512 |  | 10867.22 |  | 7219.792 |  | 11901.056
1300 |  |  |  | 2617.004 |  | 4179.7 |  | 3135.628 |  | 5104.352 |  | 3640.604 |  | 6011.944 |  | 4138.756 |  | 6905.888 |  | 4640.32 |  | 7765.712 |  | 5135.06 |  | 8673.304 |  | 5633.212 |  | 9577.484
1320 |  |  | 3391.528 |  | 5517.204 |  | 4090.988 |  | 6680.696 |  | 4766.564 |  | 7827.128 |  | 5442.14 |  | 8963.324 |  | 6104.068 |  | 10089.284 |  | 6779.644 |  | 11205.008 |  | 7444.984 |  | 12272.964
1360 |  |  | 3493.888 | 2736.424 | 5684.392 | 4370.772 | 4213.82 | 3282.344 | 6882.004 | 5339.78 | 4909.868 | 3811.204 | 8065.968 | 6288.316 | 5605.916 | 4329.828 | 9232.872 | 7226.616 | 6288.316 | 4855.276 | 10392.952 | 8123.972 | 6984.364 | 5373.9 | 11546.208 | 9072.508 | 7670.176 | 5892.524 | 12644.872 | 10017.632
1400 |  |  | 3596.248 |  | 5851.58 |  | 4336.652 |  | 7083.312 |  | 5053.172 |  | 8301.396 |  | 5769.692 |  | 9505.832 |  | 6472.564 |  | 10700.032 |  | 7189.084 |  | 11883.996 |  | 7895.368 |  | 13016.78
1420 |  |  |  | 2859.256 |  | 4565.256 |  | 3425.648 |  | 5575.208 |  | 3978.392 |  | 6564.688 |  | 4520.9 |  | 7543.932 |  | 5066.82 |  | 8482.232 |  | 5609.328 |  | 9471.712 |  | 6151.836 |  | 10461.192
1440 |  |  | 3698.608 |  | 6018.768 |  | 4462.896 |  | 7288.032 |  | 5199.888 |  | 8540.236 |  | 5936.88 |  | 9778.792 |  | 6656.812 |  | 11007.112 |  | 7393.804 |  | 12225.196 |  | 8120.56 |  | 13388.688
1480 |  |  | 3800.968 | 2978.676 | 6185.956 | 4756.328 | 4585.728 | 3568.952 | 7489.34 | 5810.636 | 5343.192 | 4145.58 | 8775.664 | 6841.06 | 6100.656 | 4711.972 | 10048.34 | 7861.248 | 6841.06 | 5281.776 | 11310.78 | 8840.492 | 7598.524 | 5848.168 | 12562.984 | 9870.916 | 8345.752 | 6414.56 | 13760.596 | 10901.34
1520 |  |  | 3906.74 |  | 6353.144 |  | 4708.56 |  | 7690.648 |  | 5486.496 |  | 9014.504 |  | 6264.432 |  | 10321.3 |  | 7028.72 |  | 11617.86 |  | 7806.656 |  | 12904.184 |  | 8574.356 |  | 14132.504
1540 |  |  |  | 3101.508 |  | 4950.812 |  | 3715.668 |  | 6049.476 |  | 4312.768 |  | 7120.844 |  | 4903.044 |  | 8181.976 |  | 5496.732 |  | 9202.164 |  | 6083.596 |  | 10273.532 |  | 6673.872 |  | 11344.9
1560 |  |  | 4009.1 |  | 6520.332 |  | 4831.392 |  | 7891.956 |  | 5629.8 |  | 9249.932 |  | 6428.208 |  | 10590.848 |  | 7212.968 |  | 11921.528 |  | 8011.376 |  | 13241.972 |  | 8799.548 |  | 14504.412
1600 |  |  | 4111.46 | 3220.928 | 6687.52 | 5141.884 | 4957.636 | 3858.972 | 8096.676 | 6284.904 | 5776.516 | 4483.368 | 9488.772 | 7397.216 | 6595.396 | 5094.116 | 10863.808 | 8499.292 | 7397.216 | 5711.688 | 12228.608 | 9560.424 | 8216.096 | 6322.436 | 13583.172 | 10672.736 | 9024.74 | 6933.184 | 14876.32 | 11785.048
1640 |  |  | 4213.82 |  | 6854.708 |  | 5080.468 |  | 8297.984 |  | 5919.82 |  | 9724.2 |  | 6759.172 |  | 11136.768 |  | 7581.464 |  | 12535.688 |  | 8420.816 |  | 13920.96 |  | 9249.932 |  | 15248.228
1660 |  |  |  | 3340.348 |  | 5336.368 |  | 4005.688 |  | 6520.332 |  | 4650.556 |  | 7673.588 |  | 5285.188 |  | 8820.02 |  | 5923.232 |  | 9918.684 |  | 6557.864 |  | 11071.94 |  | 7192.496 |  | 12228.608
1680 |  |  | 4316.18 |  | 7021.896 |  | 5203.3 |  | 8499.292 |  | 6063.124 |  | 9963.04 |  | 6922.948 |  | 11406.316 |  | 7765.712 |  | 12839.356 |  | 8625.536 |  | 14262.16 |  | 9475.124 |  | 15620.136
1720 |  |  | 4418.54 | 3463.18 | 7189.084 | 5527.44 | 5329.544 | 4148.992 | 8704.012 | 6755.76 | 6209.84 | 4817.744 | 10198.468 | 7953.372 | 7090.136 | 5476.26 | 11679.276 | 9137.336 | 7953.372 | 6138.188 | 13146.436 | 10276.944 | 8833.668 | 6796.704 | 14599.948 | 11474.556 | 9700.316 | 7451.808 | 15992.044 | 12668.756
1760 |  |  | 4520.9 |  | 7356.272 |  | 5452.376 |  | 8905.32 |  | 6353.144 |  | 10437.308 |  | 7253.912 |  | 11948.824 |  | 8137.62 |  | 13450.104 |  | 9038.388 |  | 14941.148 |  | 9925.508 |  | 16363.952
1780 |  |  |  | 3582.6 |  | 5721.924 |  | 4292.296 |  | 6991.188 |  | 4984.932 |  | 8229.744 |  | 5667.332 |  | 9454.652 |  | 6353.144 |  | 10635.204 |  | 7032.132 |  | 11873.76 |  | 7714.532 |  | 13112.316
1800 |  |  | 4623.26 |  | 7523.46 |  | 5575.208 |  | 9106.628 |  | 6496.448 |  | 10672.736 |  | 7417.688 |  | 12221.784 |  | 8321.868 |  | 13757.184 |  | 9243.108 |  | 15278.936 |  | 10150.7 |  | 16735.86
1840 |  |  | 4729.032 | 3705.432 | 7690.648 | 5912.996 | 5701.452 | 4439.012 | 9311.348 | 7226.616 | 6643.164 | 5155.532 | 10911.576 | 8506.116 | 7584.876 | 5858.404 | 12494.744 | 9775.38 | 8506.116 | 6568.1 | 14064.264 | 10993.464 | 9447.828 | 7270.972 | 15620.136 | 12272.964 | 10379.304 | 7973.844 | 17107.768 | 13555.876
1880 |  |  | 4831.392 |  | 7857.836 |  | 5824.284 |  | 9512.656 |  | 6786.468 |  | 11147.004 |  | 7748.652 |  | 12764.292 |  | 8690.364 |  | 14367.932 |  | 9652.548 |  | 15957.924 |  | 10604.496 |  | 17479.676
1900 |  |  |  | 3824.852 |  | 6107.48 |  | 4582.316 |  | 7462.044 |  | 5322.72 |  | 8785.9 |  | 6049.476 |  | 10092.696 |  | 6779.644 |  | 11351.724 |  | 7506.4 |  | 12675.58 |  | 8233.156 |  | 13996.024
1920 |  |  | 4933.752 |  | 8025.024 |  | 5947.116 |  | 9713.964 |  | 6929.772 |  | 11385.844 |  | 7912.428 |  | 13037.252 |  | 8878.024 |  | 14675.012 |  | 9860.68 |  | 16299.124 |  | 10829.688 |  | 17851.584
1960 |  |  | 5036.112 | 3944.272 | 8192.212 | 6298.552 | 6073.36 | 4729.032 | 9918.684 | 7697.472 | 7076.488 | 5489.908 | 11621.272 | 9062.272 | 8079.616 | 6240.548 | 13306.8 | 10413.424 | 9062.272 | 6994.6 | 14978.68 | 11709.984 | 10065.4 | 7745.24 | 16636.912 | 13074.784 | 11054.88 | 8492.468 | 18223.492 | 14439.584
2000 |  |  | 5138.472 |  | 8359.4 |  | 6196.192 |  | 10119.992 |  | 7219.792 |  | 11860.112 |  | 8243.392 |  | 13579.76 |  | 9246.52 |  | 15285.76 |  | 10270.12 |  | 16978.112 |  | 11280.072 |  | 18595.4
2020 |  |  |  | 4067.104 |  | 6493.036 |  | 4872.336 |  | 7932.9 |  | 5657.096 |  | 9338.644 |  | 6431.62 |  | 10730.74 |  | 7209.556 |  | 12068.244 |  | 7980.668 |  | 13473.988 |  | 8751.78 |  | 14879.732
2040 |  |  | 5240.832 |  | 8526.588 |  | 6319.024 |  | 10321.3 |  | 7363.096 |  | 12098.952 |  | 8407.168 |  | 13852.72 |  | 9430.768 |  | 15592.84 |  | 10474.84 |  | 17319.312 |  | 11505.264 |  | 18967.308
2080 |  |  | 5343.192 | 4186.524 | 8693.776 | 6684.108 | 6445.268 | 5019.052 | 10526.02 | 8168.328 | 7509.812 | 5827.696 | 12334.38 | 9615.016 | 8574.356 | 6622.692 | 14122.268 | 11051.468 | 9615.016 | 7424.512 | 15896.508 | 12426.504 | 10679.56 | 8219.508 | 17657.1 | 13873.192 | 11730.456 | 9014.504 | 19339.216 | 15323.292
2120 |  |  | 5445.552 |  | 8860.964 |  | 6568.1 |  | 10727.328 |  | 7653.116 |  | 12573.22 |  | 8738.132 |  | 14395.228 |  | 9802.676 |  | 16203.588 |  | 10887.692 |  | 17998.3 |  | 11955.648 |  | 19711.124
2140 |  |  |  | 4309.356 |  | 6878.592 |  | 5162.356 |  | 8403.756 |  | 5994.884 |  | 9894.8 |  | 6813.764 |  | 11368.784 |  | 7636.056 |  | 12784.764 |  | 8454.936 |  | 14275.808 |  | 9273.816 |  | 15763.44
2160 |  |  | 5547.912 |  | 9028.152 |  | 6690.932 |  | 10928.636 |  | 7796.42 |  | 12808.648 |  | 8901.908 |  | 14664.776 |  | 9986.924 |  | 16507.256 |  | 11092.412 |  | 18336.088 |  | 12180.84 |  | 20083.032
2200 |  |  | 5653.684 | 4428.776 | 9195.34 | 7069.664 | 6817.176 | 5305.66 | 11133.356 | 8639.184 | 7943.136 | 6162.072 | 13047.488 | 10171.172 | 9069.096 | 7004.836 | 14937.736 | 11686.1 | 10171.172 | 7851.012 | 16814.336 | 13143.024 | 11297.132 | 8693.776 | 18677.288 | 14675.012 | 12409.444 | 9533.128 | 20454.94 | 16207
2240 |  |  | 5756.044 |  | 9362.528 |  | 6940.008 |  | 11334.664 |  | 8086.44 |  | 13282.916 |  | 9232.872 |  | 15210.696 |  | 10355.42 |  | 17121.416 |  | 11501.852 |  | 19015.076 |  | 12634.636 |  | 20826.848
2260 |  |  |  | 4548.196 |  | 7264.148 |  | 5452.376 |  | 8874.612 |  | 6329.26 |  | 10447.544 |  | 7195.908 |  | 12006.828 |  | 8065.968 |  | 13501.284 |  | 8929.204 |  | 15074.216 |  | 9792.44 |  | 16647.148
2280 |  |  | 5858.404 |  | 9529.716 |  | 7062.84 |  | 11535.972 |  | 8229.744 |  | 13521.756 |  | 9396.648 |  | 15480.244 |  | 10539.668 |  | 17425.084 |  | 11706.572 |  | 19356.276 |  | 12859.828 |  | 21198.756
2320 |  |  | 5960.764 | 4671.028 | 9696.904 | 7455.22 | 7189.084 | 5595.68 | 11740.692 | 9110.04 | 8376.46 | 6499.86 | 13757.184 | 10727.328 | 9563.836 | 7386.98 | 15753.204 | 12324.144 | 10727.328 | 8280.924 | 17732.164 | 13859.544 | 11914.704 | 9168.044 | 19694.064 | 15476.832 | 13085.02 | 10051.752 | 21570.664 | 17090.708
2360 |  |  | 6063.124 |  | 9864.092 |  | 7311.916 |  | 11942 |  | 8519.764 |  | 13996.024 |  | 9727.612 |  | 16022.752 |  | 10911.576 |  | 18035.832 |  | 12119.424 |  | 20035.264 |  | 13310.212 |  | 21942.572
2380 |  |  |  | 4790.448 |  | 7649.704 |  | 5742.396 |  | 9345.468 |  | 6667.048 |  | 11003.7 |  | 7578.052 |  | 12644.872 |  | 8492.468 |  | 14217.804 |  | 9403.472 |  | 15876.036 |  | 10314.476 |  | 17530.856
2400 |  |  | 6165.484 |  | 10031.28 |  | 7434.748 |  | 12143.308 |  | 8663.068 |  | 14231.452 |  | 9891.388 |  | 16295.712 |  | 11095.824 |  | 18342.912 |  | 12324.144 |  | 20373.052 |  | 13535.404 |  | 22314.48
2440 |  |  | 6267.844 | 4913.28 | 10198.468 | 7840.776 | 7560.992 | 5885.7 | 12348.028 | 9580.896 | 8809.784 | 6834.236 | 14470.292 | 11280.072 | 10058.576 | 7769.124 | 16568.672 | 12962.188 | 11280.072 | 8707.424 | 18649.992 | 14576.064 | 12528.864 | 9642.312 | 20714.252 | 16275.24 | 13760.596 | 10573.788 | 22686.388 | 17974.416
2480 |  |  | 6370.204 |  | 10365.656 |  | 7683.824 |  | 12549.336 |  | 8953.088 |  | 14705.72 |  | 10222.352 |  | 16838.22 |  | 11464.32 |  | 18953.66 |  | 12733.584 |  | 21052.04 |  | 13985.788 |  | 23058.296
2500 |  |  |  | 5032.7 |  | 8035.26 |  | 6032.416 |  | 9819.736 |  | 7004.836 |  | 11559.856 |  | 7960.196 |  | 13282.916 |  | 8922.38 |  | 14937.736 |  | 9877.74 |  | 16677.856 |  | 10833.1 |  | 18417.976
2520 |  |  | 6475.976 |  | 10532.844 |  | 7806.656 |  | 12750.644 |  | 9096.392 |  | 14944.56 |  | 10386.128 |  | 17111.18 |  | 11651.98 |  | 19260.74 |  | 12941.716 |  | 21393.24 |  | 14214.392 |  | 23430.204
2560 |  |  | 6578.336 | 5152.12 | 10700.032 | 8229.744 | 7929.488 | 6175.72 | 12951.952 | 10055.164 | 9239.696 | 7172.024 | 15179.988 | 11836.228 | 10549.904 | 8147.856 | 17380.728 | 13600.232 | 11836.228 | 9137.336 | 19564.408 | 15295.996 | 13146.436 | 10113.168 | 21731.028 | 17077.06 | 14439.584 | 11092.412 | 23802.112 | 18858.124
2600 |  |  | 6680.696 |  | 10867.22 |  | 8055.732 |  | 13156.672 |  | 9386.412 |  | 15418.828 |  | 10717.092 |  | 17653.688 |  | 12020.476 |  | 19871.488 |  | 13351.156 |  | 22072.228 |  | 14664.776 |  | 24174.02
2620 |  |  |  | 5274.952 |  | 8420.816 |  | 6319.024 |  | 10290.592 |  | 7339.212 |  | 12112.6 |  | 8338.928 |  | 13917.548 |  | 9352.292 |  | 15654.256 |  | 10352.008 |  | 17476.264 |  | 11351.724 |  | 19301.684
2640 |  |  | 6783.056 |  | 11034.408 |  | 8178.564 |  | 13357.98 |  | 9529.716 |  | 15654.256 |  | 10880.868 |  | 17926.648 |  | 12204.724 |  | 20178.568 |  | 13555.876 |  | 22410.016 |  | 14889.968 |  | 24545.928
2680 |  |  | 6885.416 | 5394.372 | 11201.596 | 8615.3 | 8301.396 | 6465.74 | 13559.288 | 10526.02 | 9673.02 | 7506.4 | 15893.096 | 12388.972 | 11044.644 | 8530 | 18196.196 | 14238.276 | 12388.972 | 9563.836 | 20482.236 | 16012.516 | 13760.596 | 10587.436 | 22751.216 | 17875.468 | 15115.16 | 11614.448 | 24917.836 | 19741.832
2720 |  |  | 6987.776 |  | 11368.784 |  | 8427.64 |  | 13764.008 |  | 9819.736 |  | 16128.524 |  | 11211.832 |  | 18469.156 |  | 12576.632 |  | 20789.316 |  | 13968.728 |  | 23089.004 |  | 15340.352 |  | 25289.744
2740 |  |  |  | 5517.204 |  | 8806.372 |  | 6609.044 |  | 10761.448 |  | 7677 |  | 12668.756 |  | 8721.072 |  | 14555.592 |  | 9778.792 |  | 16370.776 |  | 10826.276 |  | 18278.084 |  | 11873.76 |  | 20185.392
2760 |  |  | 7090.136 |  | 11535.972 |  | 8550.472 |  | 13965.316 |  | 9963.04 |  | 16367.364 |  | 11375.608 |  | 18738.704 |  | 12760.88 |  | 21092.984 |  | 14173.448 |  | 23430.204 |  | 15565.544 |  | 25661.652
2800 |  |  | 7192.496 | 5636.624 | 11703.16 | 9000.856 | 8673.304 | 6755.76 | 14166.624 | 10996.876 | 10106.344 | 7844.188 | 16602.792 | 12945.128 | 11539.384 | 8912.144 | 19011.664 | 14876.32 | 12945.128 | 9993.748 | 21400.064 | 16729.036 | 14378.168 | 11061.704 | 23767.992 | 18677.288 | 15790.736 | 12133.072 | 26033.56 | 20625.54
2840 |  |  | 7298.268 |  | 11870.348 |  | 8799.548 |  | 14371.344 |  | 10253.06 |  | 16841.632 |  | 11706.572 |  | 19284.624 |  | 13129.376 |  | 21707.144 |  | 14582.888 |  | 24109.192 |  | 16019.34 |  | 26405.468
2860 |  |  |  | 5756.044 |  | 9191.928 |  | 6899.064 |  | 11232.304 |  | 8011.376 |  | 13221.5 |  | 9103.216 |  | 15193.636 |  | 10208.704 |  | 17087.296 |  | 11300.544 |  | 19076.492 |  | 12392.384 |  | 21069.1
2880 |  |  | 7400.628 |  | 12037.536 |  | 8922.38 |  | 14572.652 |  | 10396.364 |  | 17077.06 |  | 11870.348 |  | 19554.172 |  | 13313.624 |  | 22010.812 |  | 14787.608 |  | 24446.98 |  | 16244.532 |  | 26777.376
2920 |  |  | 7502.988 | 5878.876 | 12204.724 | 9386.412 | 9045.212 | 7042.368 | 14773.96 | 11467.732 | 10539.668 | 8178.564 | 17315.9 | 13501.284 | 12034.124 | 9294.288 | 19827.132 | 15510.952 | 13501.284 | 10420.248 | 22317.892 | 17445.556 | 14995.74 | 11535.972 | 24788.18 | 19479.108 | 16469.724 | 12651.696 | 27149.284 | 21509.248
2960 |  |  | 7605.348 |  | 12371.912 |  | 9171.456 |  | 14978.68 |  | 10686.384 |  | 17551.328 |  | 12201.312 |  | 20096.68 |  | 13685.532 |  | 22621.56 |  | 15200.46 |  | 25125.968 |  | 16694.916 |  | 27521.192
2980 |  |  |  | 5998.296 |  | 9577.484 |  | 7189.084 |  | 11703.16 |  | 8349.164 |  | 13777.656 |  | 9485.36 |  | 15831.68 |  | 10635.204 |  | 17803.816 |  | 11774.812 |  | 19878.312 |  | 12914.42 |  | 21952.808
3000 |  |  | 7707.708 |  | 12539.1 |  | 9294.288 |  | 15179.988 |  | 10829.688 |  | 17790.168 |  | 12365.088 |  | 20369.64 |  | 13869.78 |  | 22928.64 |  | 15405.18 |  | 25467.168 |  | 16920.108 |  | 27893.1