## SC Lowline W meter
Hudevad SC Lowline
Type |  |  | SCE (single) |  | SCD (double)
Height |  |  | 300
Element distance |  |  | 40 | 60 | 40 | 60
W/m at 75/65/20 |  |  | 595 | 469 | 960 | 729
n-coefficients |  |  | 1.3 | 1.3 | 1.3 | 1.3
Weight/Element |  |  | 1.1 |  | 2
Water Content/Element |  |  | 0.3 |  | 0.4
Table of heat outputs at:
Arithmetic |  |  | Logarithmic |  |  | Watt to Btu/h:
Inlet | 75 | ° C | 75 |  | 75 | 3.412
Outlet | 65 | ° C | 65 |  | 65
Ambient | 20 | ° C | 20 |  | 21
Delta T | 50 | ° C | 49.8329 |  | 48.8295
Advisory recommendation for the choice of calculation method and use of reduction factor:
Logarithmic conversion should be used on emitters up until and including height 400mm, as well as on low convectors.
The logarithmic calculation method should also be used if the relative cooling surpasses 75%.
Arithmetic conversion should be used on emitters above height 400mm if the relative cooling is under 75%.
Arithmetic outputs
W/meter | SCE single |  | SCD Double
Height | Element spacing
| 40 | 60 | 40 | 60
300 | 595 | 469 | 960 | 729
Conversion to Logarithmic Outputs
W/meter | SCE single |  | SCD Double
Height | Element spacing
| 40 | 60 | 40 | 60
300 | 579 | 457 | 935 | 710
Conversion to Btu/hr
W/meter | SCE single |  | SCD Double
Height | Element spacing
| 40 | 60 | 40 | 60
300 | 2030.14 | 1600.228 | 3275.52 | 2487.348

## SC Lowline All sizes
Hudevad SC Lowline
Type |  |  | SCE (single) |  | SCD (double)
Height |  |  | 300
Element distance |  |  | 40 | 60 | 40 | 60
W/m at 75/65/20 |  |  | 595 | 469 | 960 | 729
n-coefficients |  |  | 1.3 | 1.3 | 1.3 | 1.3
Weight/Element |  |  | 1.1 |  | 2
Water Content/Element |  |  | 0.3 |  | 0.4
Table of heat outputs at:
Arithmetic |  |  | Logarithmic |  |  | Watt to Btu/h:
Inlet | 75 | ° C | 75 |  | 75 | 3.412
Outlet | 65 | ° C | 65 |  | 65
Ambient | 20 | ° C | 20 |  | 20
Delta T | 50 | ° C | 49.8329 |  | 49.8329
Advisory recommendation for the choice of calculation method and use of reduction factor:
Logarithmic conversion should be used on emitters up until and including height 400mm, as well as on low convectors.
The logarithmic calculation method should also be used if the relative cooling surpasses 75%.
Arithmetic conversion should be used on emitters above height 400mm if the relative cooling is under 75%.
Arithmetic outputs
Type |  |  | SCE (single) |  | SCD (double)
Height |  |  | 300
Element spacing |  |  | 40 | 60 | 40 | 60
Length
400 |  |  | 238 | 188 | 384 | 292
460 |  |  |  | 216 |  | 335
480 |  |  | 286 |  | 461
560 |  |  | 333 |  | 538
580 |  |  |  | 272 |  | 423
640 |  |  | 381 | 300 | 614 | 467
700 |  |  |  | 328 |  | 510
720 |  |  | 428 |  | 691
800 |  |  | 476 |  | 768
820 |  |  |  | 385 |  | 598
880 |  |  | 524 | 413 | 845 | 642
920 |  |  | 547 |  | 883
960 |  |  | 571 |  | 922
1040 |  |  | 619 |  | 998
1060 |  |  |  | 497 |  | 773
1120 |  |  | 666 | 525 | 1075 | 816
1160 |  |  | 690 |  | 1114
1200 |  |  | 714 |  | 1152
1280 |  |  | 762 |  | 1229
1300 |  |  |  | 610 |  | 948
1360 |  |  | 809 | 638 | 1306 | 991
1420 |  |  |  | 666 |  | 1035
1440 |  |  | 857 |  | 1382
1520 |  |  | 904 |  | 1459
1540 |  |  |  | 722 |  | 1123
1600 |  |  | 952 | 750 | 1536 | 1166
1660 |  |  |  | 779 |  | 1210
1680 |  |  | 1000 |  | 1613
1760 |  |  | 1047 |  | 1690
1780 |  |  |  | 835 |  | 1298
1840 |  |  | 1095 | 863 | 1766 | 1341
1900 |  |  |  | 891 |  | 1385
1920 |  |  | 1142 |  | 1843
2000 |  |  | 1190 |  | 1920
2020 |  |  |  | 947 |  | 1473
2080 |  |  | 1238 | 976 | 1997 | 1516
2140 |  |  |  | 1004 |  | 1560
2160 |  |  | 1285 |  | 2074
2240 |  |  | 1333 |  | 2150
2260 |  |  |  | 1060 |  | 1648
2320 |  |  | 1380 | 1088 | 2227 | 1691
2380 |  |  |  | 1116 |  | 1735
2400 |  |  | 1428 |  | 2304
2480 |  |  | 1476 |  | 2381
2500 |  |  |  | 1173 |  | 1823
2560 |  |  | 1523 | 1201 | 2458 | 1866
2620 |  |  |  | 1229 |  | 1910
2640 |  |  | 1571 |  | 2534
2720 |  |  | 1618 |  | 2611
2740 |  |  |  | 1285 |  | 1997
2800 |  |  | 1666 | 1313 | 2688 | 2041
2860 |  |  |  | 1341 |  | 2085
2880 |  |  | 1714 |  | 2765
2960 |  |  | 1761 |  | 2842
2980 |  |  |  | 1398 |  | 2172
Conversion to Logarithmic Outputs
Type |  |  | SCE (single) |  | SCD (double)
Height |  |  | 300
Element spacing |  |  | 40 | 60 | 40 | 60
Length
400 |  |  | 238 | 188 | 384 | 292
460 |  |  |  | 216 |  | 335
480 |  |  | 286 |  | 461
560 |  |  | 333 |  | 538
580 |  |  |  | 272 |  | 423
640 |  |  | 381 | 300 | 614 | 467
700 |  |  |  | 328 |  | 510
720 |  |  | 428 |  | 691
800 |  |  | 476 |  | 768
820 |  |  |  | 385 |  | 598
880 |  |  | 524 | 413 | 845 | 642
920 |  |  | 547 |  | 883
960 |  |  | 571 |  | 922
1040 |  |  | 619 |  | 998
1060 |  |  |  | 497 |  | 773
1120 |  |  | 666 | 525 | 1075 | 816
1160 |  |  | 690 |  | 1114
1200 |  |  | 714 |  | 1152
1280 |  |  | 762 |  | 1229
1300 |  |  |  | 610 |  | 948
1360 |  |  | 809 | 638 | 1306 | 991
1420 |  |  |  | 666 |  | 1035
1440 |  |  | 857 |  | 1382
1520 |  |  | 904 |  | 1459
1540 |  |  |  | 722 |  | 1123
1600 |  |  | 952 | 750 | 1536 | 1166
1660 |  |  |  | 779 |  | 1210
1680 |  |  | 1000 |  | 1613
1760 |  |  | 1047 |  | 1690
1780 |  |  |  | 835 |  | 1298
1840 |  |  | 1095 | 863 | 1766 | 1341
1900 |  |  |  | 891 |  | 1385
1920 |  |  | 1142 |  | 1843
2000 |  |  | 1190 |  | 1920
2020 |  |  |  | 947 |  | 1473
2080 |  |  | 1238 | 976 | 1997 | 1516
2140 |  |  |  | 1004 |  | 1560
2160 |  |  | 1285 |  | 2074
2240 |  |  | 1333 |  | 2150
2260 |  |  |  | 1060 |  | 1648
2320 |  |  | 1380 | 1088 | 2227 | 1691
2380 |  |  |  | 1116 |  | 1735
2400 |  |  | 1428 |  | 2304
2480 |  |  | 1476 |  | 2381
2500 |  |  |  | 1173 |  | 1823
2560 |  |  | 1523 | 1201 | 2458 | 1866
2620 |  |  |  | 1229 |  | 1910
2640 |  |  | 1571 |  | 2534
2720 |  |  | 1618 |  | 2611
2740 |  |  |  | 1285 |  | 1997
2800 |  |  | 1666 | 1313 | 2688 | 2041
2860 |  |  |  | 1341 |  | 2085
2880 |  |  | 1714 |  | 2765
2960 |  |  | 1761 |  | 2842
2980 |  |  |  | 1398 |  | 2172
Conversion to Btu/hr
Type |  |  | SCE (single) |  | SCD (double)
Height |  |  | 300
Element spacing |  |  | 40 | 60 | 40 | 60
Length
400 |  |  | 812.056 | 641.456 | 1310.208 | 996.304
460 |  |  |  | 736.992 |  | 1143.02
480 |  |  | 975.832 |  | 1572.932
560 |  |  | 1136.196 |  | 1835.656
580 |  |  |  | 928.064 |  | 1443.276
640 |  |  | 1299.972 | 1023.6 | 2094.968 | 1593.404
700 |  |  |  | 1119.136 |  | 1740.12
720 |  |  | 1460.336 |  | 2357.692
800 |  |  | 1624.112 |  | 2620.416
820 |  |  |  | 1313.62 |  | 2040.376
880 |  |  | 1787.888 | 1409.156 | 2883.14 | 2190.504
920 |  |  | 1866.364 |  | 3012.796
960 |  |  | 1948.252 |  | 3145.864
1040 |  |  | 2112.028 |  | 3405.176
1060 |  |  |  | 1695.764 |  | 2637.476
1120 |  |  | 2272.392 | 1791.3 | 3667.9 | 2784.192
1160 |  |  | 2354.28 |  | 3800.968
1200 |  |  | 2436.168 |  | 3930.624
1280 |  |  | 2599.944 |  | 4193.348
1300 |  |  |  | 2081.32 |  | 3234.576
1360 |  |  | 2760.308 | 2176.856 | 4456.072 | 3381.292
1420 |  |  |  | 2272.392 |  | 3531.42
1440 |  |  | 2924.084 |  | 4715.384
1520 |  |  | 3084.448 |  | 4978.108
1540 |  |  |  | 2463.464 |  | 3831.676
1600 |  |  | 3248.224 | 2559 | 5240.832 | 3978.392
1660 |  |  |  | 2657.948 |  | 4128.52
1680 |  |  | 3412 |  | 5503.556
1760 |  |  | 3572.364 |  | 5766.28
1780 |  |  |  | 2849.02 |  | 4428.776
1840 |  |  | 3736.14 | 2944.556 | 6025.592 | 4575.492
1900 |  |  |  | 3040.092 |  | 4725.62
1920 |  |  | 3896.504 |  | 6288.316
2000 |  |  | 4060.28 |  | 6551.04
2020 |  |  |  | 3231.164 |  | 5025.876
2080 |  |  | 4224.056 | 3330.112 | 6813.764 | 5172.592
2140 |  |  |  | 3425.648 |  | 5322.72
2160 |  |  | 4384.42 |  | 7076.488
2240 |  |  | 4548.196 |  | 7335.8
2260 |  |  |  | 3616.72 |  | 5622.976
2320 |  |  | 4708.56 | 3712.256 | 7598.524 | 5769.692
2380 |  |  |  | 3807.792 |  | 5919.82
2400 |  |  | 4872.336 |  | 7861.248
2480 |  |  | 5036.112 |  | 8123.972
2500 |  |  |  | 4002.276 |  | 6220.076
2560 |  |  | 5196.476 | 4097.812 | 8386.696 | 6366.792
2620 |  |  |  | 4193.348 |  | 6516.92
2640 |  |  | 5360.252 |  | 8646.008
2720 |  |  | 5520.616 |  | 8908.732
2740 |  |  |  | 4384.42 |  | 6813.764
2800 |  |  | 5684.392 | 4479.956 | 9171.456 | 6963.892
2860 |  |  |  | 4575.492 |  | 7114.02
2880 |  |  | 5848.168 |  | 9434.18
2960 |  |  | 6008.532 |  | 9696.904
2980 |  |  |  | 4769.976 |  | 7410.864